: Access Control System

##Technical Specification & Implementation Guide

Project: Soho Hills Tower A — Project 120

Location: Dubai Hills, Dubai, UAE

Consultant: National Engineering Bureau (NEB)

Main Contractor: New System Engineering LLC

MEP Contractor: SPOTS ELECTROMECHANICAL WORKS LLC

---

#SECTION 1: INTRODUCTION

##1.1 Purpose

This document specifies the technical requirements, materials, installation methods, testing procedures, and quality standards for the Access Control System (ACS) to be installed at Project 120 — Soho Hills Tower A, Dubai Hills, Dubai, UAE.

##1.2 Scope of Work

The scope includes the supply, installation, configuration, testing, and commissioning of a complete IP-based Access Control system comprising:

- Card Readers (Proximity / Mifare)

- Magnetic Locks (600 lbs / 1200 lbs)

- Door Contacts

- Exit Buttons

- Request-to-Exit Sensors

- Door Controllers

- Power Supplies (12V DC / PoE)

- Break Glass Units

- Emergency Door Release

- Integration with Intercom & CCTV

##1.3 Applicable Standards

The installation shall comply with the following standards:

| Standard | Description |

| :--- | :--- |

| ISO/IEC 27001 | Information Security Management |

| ONVIF Profile A/C | Open Network Video Interface Forum |

| OSDP v2 | Open Supervised Device Protocol |

| Wiegand 26/34 | Access Control Interface |

| NFPA 101 | Life Safety Code |

| NFPA 731 | Standard for Installation of Premises Security |

| SIRA | Security Industry Regulatory Agency (Dubai) |

| Dubai Civil Defense | Fire & Life Safety Regulations |

| TRA / TDRA | UAE Telecommunications Regulatory Authority |

---

#SECTION 2: SYSTEM ARCHITECTURE

##2.1 Network Topology

The Access Control system shall be based on IP-based architecture with the following structure:

```

[Access Control Server]

│

[Core Network Switch]

│

┌─────────┼─────────┐

│         │         │

[Floor 1]  [Floor 2]  [Floor 3]

│         │         │

[Controller-1] [Controller-2] [Controller-3]

│         │         │

[Readers]  [Readers]  [Readers]

[Locks]    [Locks]    [Locks]

[Door Contacts] [Door Contacts] [Door Contacts]

[Exit Buttons] [Exit Buttons] [Exit Buttons]

```

##2.2 System Components

A. Card Reader

- Located at each controlled door

- Mifare 13.56 MHz

- OSDP v2 Protocol

- IP67 Rated

B. Magnetic Lock

- Located at each controlled door

- 600 lbs / 1200 lbs holding force

- Fail-Safe Operation

C. Door Contact

- Monitors door status (Open/Closed)

- Recessed or Surface Mount

D. Exit Button

- Located inside the door

- Request-to-Exit (REX)

E. Door Controller

- Controls 2 or 4 doors

- IP-based

- PoE Powered

F. Power Supply

- 12V DC / 5A

- Battery Backup

- With UPS

G. Break Glass Unit

- Emergency Door Release

- Located at each controlled door

---

#SECTION 3: MATERIAL SPECIFICATIONS

##3.1 Card Reader

| Parameter | Specification |

| :--- | :--- |

| Type | Proximity / Mifare |

| Frequency | 13.56 MHz |

| Protocol | OSDP v2 / Wiegand 26/34 |

| Read Range | 3-5 cm |

| Interface | RS-485 / Wiegand |

| Protection | IP67 / IK10 |

| Power | 12V DC |

| Operating Temp | -30°C to +65°C |

| Standard | ISO 14443A/B |

| Part Number | AC-RD-MF-001 |

##3.2 Magnetic Lock

| Parameter | Specification |

| :--- | :--- |

| Type | Electromagnetic Lock |

| Holding Force | 600 lbs (272 kg) |

| Voltage | 12V DC |

| Current | 500 mA |

| Operation | Fail-Safe |

| Monitoring | Lock Status (Optional) |

| Operating Temp | -10°C to +55°C |

| Part Number | AC-ML-600 |

##3.3 Door Contact

| Parameter | Specification |

| :--- | :--- |

| Type | Magnetic Reed Switch |

| Operation | Normally Closed (NC) |

| Voltage | 100V DC |

| Current | 0.5A |

| Mounting | Recessed / Surface |

| Part Number | AC-DC-001 |

##3.4 Exit Button

| Parameter | Specification |

| :--- | :--- |

| Type | Push Button |

| Operation | Momentary (NO/NC) |

| Voltage | 12V DC |

| Mounting | Wall Mount |

| Part Number | AC-EB-001 |

##3.5 Door Controller

| Parameter | Specification |

| :--- | :--- |

| Doors | 2 or 4 Doors |

| Readers | 2 or 4 Readers |

| Protocol | OSDP v2 / Wiegand |

| Network | 10/100 Mbps |

| Power | PoE (IEEE 802.3af) |

| Capacity | 10,000 Cards / 50,000 Events |

| Battery Backup | Yes |

| Part Number | AC-CTRL-4D |

##3.6 Power Supply

| Parameter | Specification |

| :--- | :--- |

| Output | 12V DC / 5A |

| Input | 220V AC |

| Battery | 12V / 7Ah |

| Backup Time | 4 Hours |

| Protection | Overload / Short Circuit |

| Part Number | AC-PSU-12V5A |

##3.7 Cabling

A. Reader Cable

| Parameter | Specification |

| :--- | :--- |

| Type | Cat 6 UTP / 22 AWG Shielded |

| Conductor | 22 AWG |

| Shielding | Overall Shield |

| Jacket | LSZH |

| Max Length | 150 m |

| Part Number | C06UI3-GY |

B. Lock Cable

| Parameter | Specification |

| :--- | :--- |

| Type | 2-Core × 1.5 mm² |

| Conductor | Stranded Copper |

| Jacket | LSZH |

| Max Length | 100 m |

C. Network Cable

| Parameter | Specification |

| :--- | :--- |

| Type | Cat 6 UTP |

| Jacket | LSZH |

| Standard | TIA-568-C.2 |

| Part Number | C06UI3-GY |

---

#SECTION 4: INSTALLATION PROCEDURES

##4.1 Pre-Installation

A. Site Survey

1. Verify reader locations per approved drawings

2. Check lock types (600 lbs / 1200 lbs)

3. Confirm power and network availability

4. Verify containment and pathways

5. Check door types (Wood / Metal / Glass)

B. Material Inspection

1. Check all devices against Approved Material Submittal

2. Verify firmware version

3. Check door controllers and power supplies

4. Verify cable reels and connectors

##4.2 Card Reader Installation

A. Mounting

1. Install at height 1200 mm from finished floor

2. Use supplied mounting bracket

3. Drill pilot holes and insert anchors

4. Secure bracket with stainless steel screws

5. Ensure reader is level and aligned with door

B. Cable Routing

1. Run Cat 6 cable from reader to door controller

2. Use conduit or cable tray

3. Maintain minimum bend radius: 4× cable diameter

4. Keep cables away from power lines

5. Label both ends of each cable

C. Configuration

1. Connect to controller

2. Configure reader address

3. Test card read

##4.3 Magnetic Lock Installation

A. Mounting

1. Install lock body on door frame

2. Install armature plate on door

3. Ensure alignment (gap < 3 mm)

4. Secure with screws

5. Verify holding force

B. Wiring

1. Run 2-core cable from lock to controller

2. Connect to lock output

3. Install break glass unit in parallel

4. Test lock operation

C. Configuration

1. Set lock type (Fail-Safe)

2. Configure unlock time (5 seconds)

3. Test door release

##4.4 Door Contact Installation

A. Mounting

1. Install contact on door frame

2. Install magnet on door

3. Ensure alignment (gap < 10 mm)

4. Secure with screws

B. Wiring

1. Run 2-core cable from contact to controller

2. Connect to input

3. Test door status

##4.5 Exit Button Installation

A. Mounting

1. Install at height 1200 mm from finished floor

2. Install on inside of door

3. Secure with screws

B. Wiring

1. Run 2-core cable from button to controller

2. Connect to input

3. Test door release

##4.6 Door Controller Installation

A. Rack Mounting

1. Install in 19" rack or wall mount

2. Connect to network switch

3. Connect to power (PoE or 12V DC)

B. Configuration

1. Add all readers

2. Add all locks

3. Add all door contacts

4. Add all exit buttons

5. Configure access levels

6. Configure time zones

7. Add cardholders

##4.7 Power Supply Installation

A. Mounting

1. Install in 19" rack or wall mount

2. Connect to 220V AC

3. Connect battery

4. Connect to controller

B. Configuration

1. Test battery backup

2. Test overload protection

3. Verify output voltage

##4.8 Integration with Other Systems

A. Intercom Integration

1. Configure door release signal

2. Test door unlock from indoor monitor

3. Verify event logging

B. CCTV Integration

1. Configure camera activation on door event

2. Test video feed to NVR

3. Verify recording on event

C. Fire Alarm Integration

1. Configure door release on fire alarm

2. Test fail-safe operation

3. Verify compliance with Civil Defense

---

#SECTION 5: TESTING & COMMISSIONING

##5.1 Card Reader Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Read Range | Present card | 3-5 cm |

| Read Time | Present card | < 1 second |

| Card Types | Test all cards | All read correctly |

| Tamper | Remove reader | Alarm triggered |

| IP Rating | Visual inspection | No water ingress |

##5.2 Magnetic Lock Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Holding Force | Pull door | Lock holds |

| Release Time | Trigger release | 5 seconds |

| Fail-Safe | Power off | Door unlocks |

| Break Glass | Press button | Door unlocks |

##5.3 Door Contact Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Door Closed | Close door | Status "Closed" |

| Door Open | Open door | Status "Open" |

| Forced Door | Force open | Alarm triggered |

| Door Held | Hold open | Alarm triggered |

##5.4 Controller Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Access Granted | Present valid card | Door unlocks |

| Access Denied | Present invalid card | Door remains locked |

| Anti-Passback | Enter twice | Second entry denied |

| Time Zone | Outside hours | Access denied |

| Event Log | Check log | All events recorded |

##5.5 Network Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| PoE | Check voltage | 48V DC |

| Bandwidth | Monitor | < 1 Mbps |

| Latency | Ping test | < 10 ms |

| Packet Loss | Iperf | < 0.1% |

##5.6 System Integration

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Intercom | Door release | Door unlocks |

| CCTV | Door event | Video recorded |

| Fire Alarm | Trigger alarm | Door unlocks |

---

#SECTION 6: QUALITY ASSURANCE

##6.1 Quality Control

| Activity | Responsibility | Frequency |

| :--- | :--- | :--- |

| Material Inspection | QA/QC Engineer | Every delivery |

| Reader Installation | Site Engineer | Daily |

| Lock Installation | Site Engineer | Daily |

| Cable Testing | QA/QC Engineer | 100% |

| Device Testing | QA/QC Engineer | 100% |

| System Testing | Consultant | Per milestone |

##6.2 Non-Conformance

Any non-conformance shall be:

1. Documented in NCR

2. Corrected within 7 days

3. Retested and approved

##6.3 Warranty

| Item | Warranty Period |

| :--- | :--- |

| Card Reader | 3 years |

| Magnetic Lock | 3 years |

| Door Controller | 3 years |

| Power Supply | 2 years |

| Installation | 1 year |

---

#SECTION 7: SAFETY REQUIREMENTS

##7.1 Personal Protective Equipment (PPE)

- Safety Helmet

- Safety Shoes

- Safety Glasses

- Fluorescent Vest

- Safety Gloves

- Dust Mask

##7.2 Working at Heights

1. Use scaffolding or ladders

2. Do not work alone

3. Use fall protection if > 2m

4. Barricade work area

##7.3 Electrical Safety

1. Use LOTO procedure

2. Verify no live circuits

3. Use insulated tools

4. Follow PTW system

##7.4 Emergency Procedures

1. First Aid training

2. CPR training

3. Emergency contact list

4. Fire extinguishers

##7.5 Life Safety Compliance

1. Fail-Safe locks on all egress doors

2. Break glass units at each door

3. Integration with Fire Alarm

4. Compliance with NFPA 101

5. Approval from Dubai Civil Defense

---

#SECTION 8: PROJECT SCHEDULE

| Phase | Duration | Milestone |

| :--- | :--- | :--- |

| Mobilization | 1 week | Site setup |

| Containment | 2 weeks | Cable trays |

| Cable Pulling | 3 weeks | All cables |

| Reader Installation | 2 weeks | All readers |

| Lock Installation | 2 weeks | All locks |

| Controller Setup | 1 week | Configured |

| Testing | 2 weeks | 100% tested |

| Commissioning | 1 week | Handover |

| Total | 14 weeks | |

---

#SECTION 9: DOCUMENTATION

##9.1 Submittals

1. Material Submittal (Approved)

2. Shop Drawings (Approved)

3. Method Statement (Approved)

4. Testing & Commissioning Statement

##9.2 As-Built Documentation

1. As-Built Drawings (CAD)

2. Device Schedule (Excel)

3. Test Reports (PDF)

4. IP Address Schedule

5. Access Level Matrix

6. Warranty Certificates

7. O&M Manual

---

#SECTION 10: APPENDICES

##Appendix A: Device Schedule (Example)

| Device ID | Location | Type | IP Address |

| :--- | :--- | :--- | :--- |

| AC-RD-01 | Main Entrance | Reader | 192.168.3.101 |

| AC-RD-02 | Parking Entrance | Reader | 192.168.3.102 |

| AC-RD-03 | Gym Entrance | Reader | 192.168.3.103 |

| AC-ML-01 | Main Entrance | Lock | — |

| AC-ML-02 | Parking Entrance | Lock | — |

| AC-CTRL-01 | MTR | Controller | 192.168.3.10 |

##Appendix B: Access Level Matrix

| Access Level | Doors | Time Zone | Cardholders |

| :--- | :--- | :--- | :--- |

| Level 1 (Resident) | Main Entrance, Flat Door | 24/7 | Residents |

| Level 2 (Staff) | Main Entrance, Service Door | 06:00-22:00 | Staff |

| Level 3 (Admin) | All Doors | 24/7 | Admin |

| Level 4 (Visitor) | Main Entrance Only | 08:00-20:00 | Visitors |

##Appendix C: Cable Schedule (Example)

| Cable ID | From | To | Type | Length |

| :--- | :--- | :--- | :--- | :--- |

| AC-C-001 | AC-CTRL-01 | AC-RD-01 | Cat 6 UTP | 45m |

| AC-C-002 | AC-CTRL-01 | AC-ML-01 | 2-Core × 1.5mm² | 45m |

| AC-C-003 | AC-CTRL-01 | AC-DC-01 | 2-Core × 0.5mm² | 45m |

| AC-C-004 | AC-CTRL-01 | AC-EB-01 | 2-Core × 0.5mm² | 45m |

##Appendix D: IP Address Schedule

| Device | IP Range | VLAN |

| :--- | :--- | :--- |

| Readers | 192.168.3.100-150 | 40 |

| Controllers | 192.168.3.10-20 | 40 |

| Server | 192.168.3.5-9 | 40 |

| Clients | 192.168.3.30-50 | 40 |

##Appendix E: Test Report Format

| Door ID | Card Read | Lock | Door Contact | Exit Button | Result |

| :--- | :--- | :--- | :--- | :--- | :--- |

| D-01 | PASS | PASS | PASS | PASS | ✅ |

| D-02 | PASS | PASS | PASS | PASS | ✅ |

| D-03 | PASS | PASS | PASS | PASS | ✅ |

##Appendix F: Troubleshooting Guide

| Problem | Possible Cause | Solution |

| :--- | :--- | :--- |

| Card Not Reading | Reader issue | Check wiring |

| Door Not Unlocking | Lock issue | Check power |

| Door Not Closing | Door contact issue | Check alignment |

| Access Denied | Card not programmed | Add card to system |

| Controller Offline | Network issue | Check cable |

---

END OF DOCUMENT

Document Reference: SPOTS-120-ACCESS-SPEC-001

Revision: R00

Date: September 2026

Prepared by: SPOTS ELECTROMECHANICAL WORKS LLC

---