📚 محتوى نصي كامل لـ 4 ملفات PDF — مشروع 120 (Soho Hills Tower A)

سأكتب المحتوى في 4 ردود منفصلة (كل ملف في رد). كل ملف محتوى احترافي كامل جاهز للتحويل إلى PDF.

---

📄 الملف 1: Structured Cabling System (SCS)

Technical Specification & Implementation Guide

Project: Soho Hills Tower A — Project 120

Location: Dubai Hills, Dubai, UAE

Consultant: National Engineering Bureau (NEB)

Main Contractor: New System Engineering LLC

MEP Contractor: SPOTS ELECTROMECHANICAL WORKS LLC

---

SECTION 1: INTRODUCTION

1.1 Purpose

This document specifies the technical requirements, materials, installation methods, testing procedures, and quality standards for the Structured Cabling System (SCS) to be installed at Project 120 — Soho Hills Tower A, Dubai Hills, Dubai, UAE.

1.2 Scope of Work

The scope includes the supply, installation, termination, testing, labeling, and commissioning of a complete end-to-end structured cabling system comprising:

- Fiber optic backbone cables (Single-mode OS2)

- UTP Cat 6 horizontal copper cables

- Fiber termination boxes (4-port)

- Consolidation cabinets (12U)

- Main Telecom Room (MTR) equipment

- GPON splitters (2x32)

- Patch panels (Copper & Fiber)

- All associated containment, pathways, and accessories

1.3 Applicable Standards

The installation shall comply with the following standards:

| Standard | Description |

| :--- | :--- |

| ISO/IEC 11801 | Generic Cabling for Customer Premises |

| EN 50173-1 | Information Technology — Generic Cabling |

| ANSI/TIA-568-C.2 | Commercial Building Telecommunications Cabling |

| ANSI/TIA-569 | Commercial Building Standard for Pathways and Spaces |

| TIA/EIA TSB-72 | Centralized Optical Fiber Cabling Guidelines |

| TIA/EIA TSB-75 | Additional Horizontal Cabling Practices |

| IEC 60364-1 | Electrical Installations of Buildings |

| IEC 60950 | Safety of Information Technology Equipment |

| TRA / TDRA | UAE Telecommunications Regulatory Authority Requirements |

| Etisalat / du | UAE Telecom Operators Guidelines |

---

SECTION 2: SYSTEM ARCHITECTURE

2.1 Network Topology

The structured cabling system shall be based on a star topology with the following hierarchy:

```

[Main Telecom Room (MTR)]

│

┌────────┼────────┐

│        │        │

[MTR Rack] [ODF]  [Splitters]

│        │        │

┌────┴────┬───┴────┬───┴────┐

│         │        │        │

[Floor 1] [Floor 2] [Floor 3] ... [Floor N]

│         │        │        │

[12U CP]  [12U CP] [12U CP] [12U CP]

│         │        │        │

[TO]      [TO]     [TO]     [TO]

```

2.2 System Components

A. Main Telecom Room (MTR)

- Located on Ground Floor or Basement

- Minimum dimensions: 3m × 3m × 3m

- Contains: 42U Floor Standing Rack, ODF, GPON Splitters, UPS

B. Floor Distributor (FD)

- Located on each floor

- Contains: 12U Wall Mount Cabinet

- Serves up to 3 floors per Mini ODF

C. Consolidation Point (CP)

- Located inside each apartment

- 12U Home Consolidation Cabinet

- Contains: Fiber Terminal Box, Copper Patch Panel, Power Socket

D. Telecommunications Outlet (TO)

- Located in each room

- Dual RJ45 Outlet with shutter

- Single-mode Fiber Outlet (optional)

---

SECTION 3: MATERIAL SPECIFICATIONS

3.1 Cat 6 UTP Copper Cable

| Parameter | Specification |

| :--- | :--- |

| Category | Cat 6 |

| Conductor | Solid Bare Copper |

| Conductor Size | 23 AWG |

| Insulation | HDPE |

| Pairs | 4 Twisted Pairs |

| Jacket Material | LSZH (Low Smoke Zero Halogen) |

| Jacket Color | Grey (GY) |

| External Diameter | 6.3 ± 0.3 mm |

| Frequency | Up to 250 MHz |

| Impedance | 100 ± 15 Ω (1-100 MHz) |

| DC Resistance | ≤ 9.5 Ω/100m |

| Mutual Capacitance | < 55 pF/m |

| Propagation Delay Skew | < 20 ns/100m |

| Part Number | C06UI3-GY |

Performance Standards:

- ISO/IEC 11801

- TIA-568-C.2

- EN 50288-6-1:2013

- IEC 60332-1-2 (Flame Retardant)

- IEC 61034-1/2 (Smoke Density)

- IEC 60754-2 (Halogen Content)

3.2 Fiber Optic Cable (Single-Mode OS2)

A. Backbone Fiber Cable (48-Core)

| Parameter | Specification |

| :--- | :--- |

| Fiber Type | Single-Mode OS2 |

| Standard | ITU-T G.657.A1/A2 |

| Backward Compatible | ITU-T G.652.D |

| Core Diameter | 9 µm |

| Cladding Diameter | 125 ± 1.0 µm |

| Coating Diameter | 245 ± 10 µm |

| Attenuation @1310nm | ≤ 0.4 dB/km |

| Attenuation @1550nm | ≤ 0.3 dB/km |

| Jacket Material | LSZH |

| Fiber Count | 48 cores |

| Part Number | FCOS2-48-MTBI-3 |

B. Drop Fiber Cable (4-Core)

| Parameter | Specification |

| :--- | :--- |

| Fiber Type | Single-Mode OS2 |

| Fiber Count | 4 cores |

| Cable Type | FTTH Drop Cable |

| Cross Section | Flat |

| Strength Member | FRP (Fiberglass Reinforced Plastic) |

| Jacket Material | LSZH |

| Bend Radius | 10× Cable Diameter |

| Part Number | FCOS2-04-DRPI-3 |

3.3 Fiber Connectors

A. SC/APC Connector

| Parameter | Specification |

| :--- | :--- |

| Type | SC/APC (Angled Physical Contact) |

| Insertion Loss | < 0.10 dB |

| Return Loss | ≥ 60 dB |

| Durability | 1000 mating cycles |

| Operating Temp | -20°C to +75°C |

| Standard | IEC 61754 |

| Part Number | A-SCAS-C |

B. LC/APC Connector

| Parameter | Specification |

| :--- | :--- |

| Type | LC/APC |

| Insertion Loss | < 0.10 dB |

| Return Loss | ≥ 60 dB |

| Durability | 1000 mating cycles |

| Part Number | A-LCAD-C |

3.4 Copper Connectors

Cat 6 Keystone Jack

| Parameter | Specification |

| :--- | :--- |

| Category | Cat 6 |

| Type | Unshielded RJ45 |

| Angle | 180° |

| Wire Gauge | AWG 22-26 |

| Insertion Life | 750 cycles minimum |

| Dielectric Strength | AC 750V / DC 1000V |

| Contact Material | Phosphor Bronze |

| Standard | ISO/IEC 11801, TIA/EIA 568C |

| Part Number | M06U180 |

3.5 Patch Panels

A. Copper Patch Panel (24-Port)

| Parameter | Specification |

| :--- | :--- |

| Ports | 24 |

| Type | Unshielded |

| Size | 19" 1U |

| Cable Management | Brush Type |

| Part Number | PP06U24-UL |

B. Fiber Patch Panel (48-Port)

| Parameter | Specification |

| :--- | :--- |

| Ports | 48 |

| Type | SC Simplex / LC Duplex |

| Size | 19" 2U |

| Splice Cassette | 48-way |

| Part Number | E-P-48-SC |

3.6 Cabinets

A. Floor Standing Cabinet (42U)

| Parameter | Specification |

| :--- | :--- |

| Height | 42U |

| Width | 800 mm |

| Depth | 800 mm |

| Front Door | Glass Single Door |

| Rear Door | Steel Sheet Single Door |

| Side Panels | Included |

| Mounting | 19" Angles |

| Castors | Yes |

| Fan Tray | 4-Way on Top |

| Part Number | FS428811-9004 |

B. Wall Mount Cabinet (12U)

| Parameter | Specification |

| :--- | :--- |

| Height | 12U |

| Width | 600 mm |

| Depth | 150 mm (Flush) / 300 mm (Wall) |

| Front Door | Glass Door |

| Color | RAL 7035 |

| Part Number | WMONUF12615-7035 |

3.7 GPON Splitters

| Parameter | Specification |

| :--- | :--- |

| Type | Planar Lightwave Circuit (PLC) |

| Configuration | 2×32 |

| Connector Type | SC/APC (Etisalat) / LC/APC (du) |

| Operating Wavelength | 1260 - 1635 nm |

| Insertion Loss | ≤ 18 dB |

| Operating Temp | -24°C to +85°C |

| Standard | Telcordia GR-1209, GR-1221 |

| Part Number | SPSCRM2321.5 (Etisalat) / SPLCRM2321.5 (du) |

---

SECTION 4: INSTALLATION PROCEDURES

4.1 Pre-Installation

A. Site Survey

1. Verify all pathways and containment are installed per approved drawings

2. Check that all cable trays, conduits, and pull boxes are in place

3. Confirm MTR, FTR, and CP locations

4. Verify electrical supply (13A twin socket) in each CP

B. Material Inspection

1. Check all materials against the Approved Material Submittal

2. Verify cable reels for damage and correct lengths

3. Check continuity of fiber optic cables (Pre-installation testing)

4. Verify all connectors and patch panels

4.2 Copper Cable Installation

A. Cable Pulling

1. Verify cable pathway is free from sharp bends

2. Use cable rollers at corners

3. Maintain minimum bend radius: 4× cable diameter (25 mm)

4. Maximum pulling tension: 110 N (25 lbf)

5. Do not exceed 90 meters from patch panel to outlet

B. Cable Support

1. Use cable trays or baskets for horizontal runs

2. Maximum 60 cables per 100×50 mm tray

3. Support cables every 1.5 meters

4. Use Velcro ties (not plastic zip ties)

C. Cable Separation

1. Maintain minimum 300 mm separation from power cables

2. Cross power cables at 90° angle

3. Use separate conduits for telecom and power

D. Cable Labeling

1. Label both ends of each cable

2. Use unique identifier per approved labeling scheme

3. Machine-printed labels only

4.3 Fiber Optic Cable Installation

A. Pre-Installation Testing

1. Test each fiber reel with OTDR

2. Verify attenuation < 0.4 dB/km @1310nm

3. Document results

B. Cable Pulling

1. Maximum pulling tension: 100 N (short-term)

2. Minimum bend radius: 20× cable diameter (during installation)

3. Minimum bend radius: 10× cable diameter (after installation)

4. Use fiber optic lubricant if needed

C. Fiber Splicing

1. Use fusion splicer for all splices

2. Splice loss < 0.1 dB

3. Protect splices with splice protectors

4. Store in splice trays

D. Fiber Termination

1. Terminate in 4-port fiber terminal box

2. Use SC/APC pigtails for Etisalat

3. Use LC/APC pigtails for du

4. Clean all connectors before mating

4.4 Cabinet Installation

A. Floor Standing Cabinet

1. Install on raised floor or concrete base

2. Level and secure with anchor bolts

3. Install cable management (brush panels)

4. Install PDU (6-way horizontal)

5. Connect earth bonding

B. Wall Mount Cabinet

1. Install at height 1200 mm from finished floor

2. Secure to wall with anchor bolts

3. Ensure front door opens fully

4. Connect earth bonding

C. Home Consolidation Cabinet

1. Install inside each apartment near entrance

2. Height: 1200 mm from FFL

3. Do not install in kitchen, laundry, or bedroom

4. Ensure 13A power socket inside cabinet

5. Lockable front door

---

SECTION 5: TESTING & COMMISSIONING

5.1 Copper Cable Testing

A. Test Equipment

- Fluke DSX-5000 CableAnalyzer (Level II Tester)

- Calibrated per ISO/IEC 11801

B. Test Parameters

1. Wire Map

2. Length

3. Insertion Loss (Attenuation)

4. Return Loss

5. NEXT (Near-End Crosstalk)

6. PSNEXT (Power Sum NEXT)

7. ELFEXT (Equal Level Far-End Crosstalk)

8. PSELFEXT

9. ACR (Attenuation to Crosstalk Ratio)

10. PSACR

11. Delay Skew

12. Impedance

13. DC Loop Resistance

C. Pass/Fail Criteria

- All tests must PASS per Cat 6 limits

- 100% of installed links tested

- Failed links must be repaired and retested

D. Documentation

- Save results in Fluke LinkWare software

- Export to PDF for submission

- Submit to consultant for approval

5.2 Fiber Optic Testing

A. Test Equipment

- OTDR (Optical Time Domain Reflectometer)

- Light Source & Power Meter

B. Test Parameters

1. Continuity

2. Length

3. Attenuation @ 1310nm and 1550nm

4. Splice Loss

5. Connector Loss

6. Return Loss

C. Test Method

- Light Source + Power Meter: One direction (sufficient)

- OTDR: Both directions (required)

- Test 100% of installed fibers

D. Pass/Fail Criteria

- Attenuation ≤ design loss budget

- Splice Loss ≤ 0.1 dB

- Connector Loss ≤ 0.3 dB

5.3 System Commissioning

A. Visual Inspection

1. Verify all outlets are labeled

2. Verify all cables are dressed properly

3. Verify all connectors are clean

4. Verify earth bonding is complete

B. Functional Testing

1. Connect patch cords and verify link

2. Test IP connectivity (if applicable)

3. Verify GPON splitter operation

C. Documentation

1. As-Built Drawings

2. Test Reports (Copper + Fiber)

3. Labeling Schedule

4. Warranty Certificate

---

SECTION 6: QUALITY ASSURANCE

6.1 Quality Control

| Activity | Responsibility | Frequency |

| :--- | :--- | :--- |

| Material Inspection | QA/QC Engineer | Every delivery |

| Cable Pulling Inspection | Site Engineer | Daily |

| Termination Inspection | QA/QC Engineer | Per floor |

| Testing | QA/QC Engineer | 100% links |

| Final Inspection | Consultant | Per milestone |

6.2 Non-Conformance

Any non-conformance shall be:

1. Documented in NCR (Non-Conformance Report)

2. Corrected within 7 days

3. Retested and approved

6.3 Warranty

| Item | Warranty Period |

| :--- | :--- |

| Product Warranty | 1 year from TOC |

| Performance Warranty | 25 years from TOC |

| Installation Warranty | 1 year from TOC |

---

SECTION 7: SAFETY REQUIREMENTS

7.1 Personal Protective Equipment (PPE)

- Safety Helmet

- Safety Shoes

- Safety Glasses

- Fluorescent Vest

- Safety Gloves

- Dust Mask (when required)

7.2 Working at Heights

1. Use scaffolding or ladders (approved)

2. Do not work alone

3. Use fall protection if > 2m

4. Barricade work area

7.3 Electrical Safety

1. Use LOTO (Lock-Out Tag-Out) procedure

2. Verify no live circuits

3. Use insulated tools

4. Follow PTW (Permit to Work) system

7.4 Emergency Procedures

1. First Aid training for all technicians

2. CPR training

3. Emergency contact list posted

4. Fire extinguishers available

---

SECTION 8: PROJECT SCHEDULE

| Phase | Duration | Milestone |

| :--- | :--- | :--- |

| Mobilization | 1 week | Site setup |

| Containment Installation | 4 weeks | Cable trays installed |

| Copper Cable Pulling | 6 weeks | All Cat 6 installed |

| Fiber Cable Pulling | 4 weeks | All fiber installed |

| Termination | 4 weeks | All connectors terminated |

| Testing | 3 weeks | 100% links tested |

| Commissioning | 1 week | System handed over |

| Total | 23 weeks | |

---

SECTION 9: DOCUMENTATION

9.1 Submittals

1. Material Submittal (Approved)

2. Shop Drawings (Approved)

3. Method Statement (Approved)

4. Testing & Commissioning Statement

9.2 As-Built Documentation

1. As-Built Drawings (CAD)

2. Cable Schedule (Excel)

3. Test Reports (PDF)

4. Labeling Schedule

5. Warranty Certificates

6. Operation & Maintenance Manual

---

SECTION 10: APPENDICES

Appendix A: Cable Schedule (Example)

| Cable ID | From | To | Type | Length |

| :--- | :--- | :--- | :--- | :--- |

| C-001 | MTR-ODF-1 | FTR-1F-MiniODF | 48C SM | 85m |

| C-002 | FTR-1F-MiniODF | CP-101 | 4C SM | 45m |

| C-003 | FTR-1F-MiniODF | CP-102 | 4C SM | 52m |

| D-001 | CP-101 | TO-101-A | Cat 6 UTP | 25m |

| D-002 | CP-101 | TO-101-B | Cat 6 UTP | 30m |

Appendix B: Labeling Scheme

Cable Labels:

```

[Project Code]-[Floor]-[Type]-[Number]

Example: 120-1F-C-001

```

Outlet Labels:

```

[Flat Number]-[Room]-[Port]

Example: 101-BED1-A

```

Appendix C: Test Report Format

| Link ID | Length | NEXT | Attenuation | Return Loss | Result |

| :--- | :--- | :--- | :--- | :--- | :--- |

| 101-A | 25.3m | 45.2 dB | 18.5 dB | 22.1 dB | PASS |

| 101-B | 30.1m | 43.8 dB | 19.2 dB | 21.5 dB | PASS |

---

END OF DOCUMENT

Document Reference: SPOTS-120-SCS-SPEC-001

Revision: R00

Date: September 2026

Prepared by: SPOTS ELECTROMECHANICAL WORKS LLC