# 📄 الملف 2: CCTV System

### Technical Specification & Implementation Guide

Project: Soho Hills Tower A — Project 120

Location: Dubai Hills, Dubai, UAE

Consultant: National Engineering Bureau (NEB)

Main Contractor: New System Engineering LLC

MEP Contractor: SPOTS ELECTROMECHANICAL WORKS LLC

---

## SECTION 1: INTRODUCTION

### 1.1 Purpose

This document specifies the technical requirements, materials, installation methods, testing procedures, and quality standards for the CCTV Surveillance System to be installed at Project 120 — Soho Hills Tower A, Dubai Hills, Dubai, UAE.

### 1.2 Scope of Work

The scope includes the supply, installation, configuration, testing, and commissioning of a complete IP-based CCTV system comprising:

- IP Cameras (Bullet, Dome, PTZ)

- Network Video Recorder (NVR)

- Hard Disk Drives (HDD) for storage

- PoE Switches

- Cat 6 UTP Cabling

- Fiber Optic Backbone

- Video Management Software (VMS)

- Monitor Display & Control Room Equipment

### 1.3 Applicable Standards

The installation shall comply with the following standards:

| Standard | Description |

| :--- | :--- |

| ISO/IEC 27001 | Information Security Management |

| ONVIF Profile S | Open Network Video Interface Forum |

| ANSI/TIA-568-C.2 | Commercial Building Telecommunications Cabling |

| IEC 60529 | IP Rating (Ingress Protection) |

| NFPA 731 | Standard for Installation of Premises Security |

| SIRA | Security Industry Regulatory Agency (Dubai) |

| Dubai Police | CCTV Regulations & Guidelines |

| TRA / TDRA | UAE Telecommunications Regulatory Authority |

---

## SECTION 2: SYSTEM ARCHITECTURE

### 2.1 Network Topology

The CCTV system shall be based on IP-based architecture with the following structure:

```

[Control Room / Security Room]

│

┌─────────┼─────────┐

│         │         │

[NVR]    [VMS Server] [Monitor Wall]

│         │         │

└─────────┼─────────┘

│

[Core Switch]

│

┌─────────┼─────────┐

│         │         │

[PoE SW-1] [PoE SW-2] [PoE SW-3]

│         │         │

[Floor 1]  [Floor 2]  [Floor 3]

│         │         │

[Cameras]  [Cameras]  [Cameras]

```

### 2.2 System Components

A. IP Cameras

- Bullet Cameras (Outdoor)

- Dome Cameras (Indoor)

- PTZ Cameras (Coverage Areas)

- Fisheye Cameras (360°)

B. Network Video Recorder (NVR)

- 64-Channel NVR

- RAID Storage

- Redundant Power Supply

C. Storage

- 10 TB HDD × 4 (RAID 5)

- Total: 30 TB Usable

- Retention: 30 Days

D. PoE Switches

- 24-Port PoE+ Switch

- 48-Port PoE+ Switch

- Uplink: Fiber Optic

E. Video Management Software (VMS)

- ONVIF Compliant

- Multi-Server Support

- Mobile App Access

---

## SECTION 3: MATERIAL SPECIFICATIONS

### 3.1 IP Cameras

A. Bullet Camera (Outdoor)

| Parameter | Specification |

| :--- | :--- |

| Resolution | 4K (8MP) |

| Lens | 2.8-12mm Motorized |

| IR Range | 30-50m |

| IP Rating | IP67 |

| Vandal Proof | IK10 |

| WDR | 120 dB |

| Compression | H.265+ |

| PoE | IEEE 802.3af |

| Operating Temp | -30°C to +60°C |

| Standard | ONVIF Profile S |

B. Dome Camera (Indoor)

| Parameter | Specification |

| :--- | :--- |

| Resolution | 4MP (2K) |

| Lens | 2.8mm Fixed |

| IR Range | 20-30m |

| IP Rating | IP66 |

| Vandal Proof | IK10 |

| WDR | 120 dB |

| PoE | IEEE 802.3af |

| Standard | ONVIF Profile S |

C. PTZ Camera

| Parameter | Specification |

| :--- | :--- |

| Resolution | 4MP |

| Optical Zoom | 25× |

| Pan Range | 360° |

| Tilt Range | -15° to +90° |

| IR Range | 100m |

| IP Rating | IP67 |

| PoE | IEEE 802.3at |

| Standard | ONVIF Profile S |

### 3.2 Network Video Recorder (NVR)

| Parameter | Specification |

| :--- | :--- |

| Channels | 64 IP Channels |

| Bandwidth | 320 Mbps Incoming |

| HDD Bays | 8 SATA Bays |

| RAID | RAID 0/1/5/6/10 |

| Video Output | HDMI × 2, VGA × 1 |

| Resolution | Up to 12MP |

| Compression | H.265+/H.265/H.264 |

| Network | 2× Gigabit Ethernet |

| Power | Redundant PSU |

| Standard | ONVIF Profile S/G |

### 3.3 Hard Disk Drives (HDD)

| Parameter | Specification |

| :--- | :--- |

| Capacity | 10 TB |

| Type | Surveillance HDD |

| Interface | SATA 6 Gb/s |

| Cache | 256 MB |

| RPM | 7200 |

| Workload | 24/7 Continuous |

| MTBF | 1.5 Million Hours |

### 3.4 PoE Switches

A. 24-Port PoE+ Switch

| Parameter | Specification |

| :--- | :--- |

| Ports | 24× PoE+ (10/100/1000) |

| Uplink | 4× SFP+ |

| PoE Budget | 370W |

| Standard | IEEE 802.3at |

| Managed | Layer 2+ |

| VLAN | 802.1Q |

| QoS | 802.1p |

B. 48-Port PoE+ Switch

| Parameter | Specification |

| :--- | :--- |

| Ports | 48× PoE+ (10/100/1000) |

| Uplink | 4× SFP+ |

| PoE Budget | 740W |

| Standard | IEEE 802.3at |

| Managed | Layer 2+ |

### 3.5 Cabling

A. Horizontal Cabling

| Parameter | Specification |

| :--- | :--- |

| Type | Cat 6 UTP |

| Conductor | 23 AWG Solid Bare Copper |

| Jacket | LSZH |

| Standard | TIA-568-C.2 |

| Max Length | 90 m |

| Part Number | C06UI3-GY |

B. Backbone Cabling

| Parameter | Specification |

| :--- | :--- |

| Type | Single-Mode Fiber OS2 |

| Cores | 12 Cores |

| Connector | LC/APC |

| Standard | ITU-T G.652.D |

| Part Number | FCOS2-12-MTBI-3 |

### 3.6 Video Management Software (VMS)

| Parameter | Specification |

| :--- | :--- |

| License | 64-Channel |

| Support | ONVIF Compliant |

| Features | Live View, Playback, Motion Detection |

| Mobile App | iOS / Android |

| Storage | Centralized |

| Backup | Automatic |

| Integration | Access Control, Intercom |

---

## SECTION 4: INSTALLATION PROCEDURES

### 4.1 Pre-Installation

A. Site Survey

1. Verify camera locations per approved drawings

2. Check lighting conditions and field of view

3. Confirm power and network availability

4. Verify containment and pathways

B. Material Inspection

1. Check all cameras against Approved Material Submittal

2. Verify firmware version

3. Check PoE switches and NVR

4. Verify cable reels and connectors

### 4.2 Camera Installation

A. Mounting

1. Use supplied mounting bracket

2. Drill pilot holes and insert anchors

3. Secure bracket with stainless steel screws

4. Ensure bracket is level and rated for camera weight

5. For ceiling mount, ensure ceiling can support weight

B. Cable Routing

1. Run Cat 6 cable from camera to nearest PoE switch

2. Use conduit or cable tray

3. Maintain minimum bend radius: 4× cable diameter

4. Keep cables away from power lines

5. Label both ends of each cable

C. Power & Connectivity

1. For PoE cameras: connect to PoE switch

2. For non-PoE: install 12V/24V power supply

3. Reserve IP address in DHCP or assign static

4. Verify camera boots up

D. Camera Alignment

1. Access camera web interface

2. Adjust pan/tilt/zoom (if applicable)

3. Set focus (manual or auto)

4. Verify image quality day/night

5. Configure motion detection zones

### 4.3 NVR Installation

A. Rack Mounting

1. Install NVR in 19" rack

2. Secure with screws

3. Connect to network switch

4. Connect to monitor (HDMI)

B. HDD Installation

1. Install HDDs in bays

2. Configure RAID 5

3. Initialize HDDs

4. Verify storage capacity

C. Configuration

1. Add cameras to NVR

2. Configure recording schedule

3. Set motion detection

4. Configure user accounts

5. Set up backup schedule

### 4.4 PoE Switch Installation

A. Rack Mounting

1. Install in 19" rack

2. Connect to core switch (fiber uplink)

3. Connect to power (UPS)

B. Configuration

1. Configure VLANs

2. Set up QoS

3. Configure PoE budget

4. Enable SNMP monitoring

### 4.5 VMS Installation

A. Server Setup

1. Install VMS server

2. Configure storage

3. Add cameras

4. Set up user permissions

B. Client Setup

1. Install VMS client on operator PCs

2. Configure monitor wall

3. Set up alerts

---

## SECTION 5: TESTING & COMMISSIONING

### 5.1 Camera Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Video Quality | Live view | Clear, no distortion |

| Resolution | Check settings | 4MP or higher |

| Night Vision | Test in dark | IR works |

| Motion Detection | Trigger motion | Alert generated |

| Recording | Playback | Video recorded |

| Remote Access | Mobile app | Accessible |

### 5.2 NVR Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Recording | Playback | Continuous recording |

| Storage | Check HDD | RAID 5 active |

| Retention | Check oldest | ≥ 30 days |

| Backup | Test restore | Successful |

| Redundancy | Failover test | No data loss |

### 5.3 Network Testing

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| PoE | Check voltage | 48V DC |

| Bandwidth | Monitor | < 320 Mbps |

| Latency | Ping test | < 10 ms |

| Packet Loss | Iperf | < 0.1% |

### 5.4 System Integration

| Test | Method | Pass Criteria |

| :--- | :--- | :--- |

| Access Control | Door event | Video triggered |

| Intercom | Doorbell | Video triggered |

| Alarm | Trigger alarm | Video recorded |

| VMS | Live view | All cameras visible |

---

## SECTION 6: QUALITY ASSURANCE

### 6.1 Quality Control

| Activity | Responsibility | Frequency |

| :--- | :--- | :--- |

| Material Inspection | QA/QC Engineer | Every delivery |

| Camera Installation | Site Engineer | Daily |

| Cable Testing | QA/QC Engineer | 100% |

| Camera Testing | QA/QC Engineer | 100% |

| System Testing | Consultant | Per milestone |

### 6.2 Non-Conformance

Any non-conformance shall be:

1. Documented in NCR

2. Corrected within 7 days

3. Retested and approved

### 6.3 Warranty

| Item | Warranty Period |

| :--- | :--- |

| Cameras | 3 years |

| NVR | 3 years |

| HDD | 5 years |

| Switches | 5 years |

| Installation | 1 year |

---

## SECTION 7: SAFETY REQUIREMENTS

### 7.1 Personal Protective Equipment (PPE)

- Safety Helmet

- Safety Shoes

- Safety Glasses

- Fluorescent Vest

- Safety Gloves

- Dust Mask

### 7.2 Working at Heights

1. Use scaffolding or ladders

2. Do not work alone

3. Use fall protection if > 2m

4. Barricade work area

### 7.3 Electrical Safety

1. Use LOTO procedure

2. Verify no live circuits

3. Use insulated tools

4. Follow PTW system

### 7.4 Emergency Procedures

1. First Aid training

2. CPR training

3. Emergency contact list

4. Fire extinguishers

---

## SECTION 8: PROJECT SCHEDULE

| Phase | Duration | Milestone |

| :--- | :--- | :--- |

| Mobilization | 1 week | Site setup |

| Containment | 2 weeks | Cable trays |

| Cable Pulling | 4 weeks | All Cat 6 |

| Camera Installation | 3 weeks | All cameras |

| NVR & Server | 2 weeks | Configured |

| Testing | 2 weeks | 100% tested |

| Commissioning | 1 week | Handover |

| Total | 15 weeks | |

---

## SECTION 9: DOCUMENTATION

### 9.1 Submittals

1. Material Submittal (Approved)

2. Shop Drawings (Approved)

3. Method Statement (Approved)

4. Testing & Commissioning Statement

### 9.2 As-Built Documentation

1. As-Built Drawings (CAD)

2. Camera Schedule (Excel)

3. Test Reports (PDF)

4. IP Address Schedule

5. VMS Configuration

6. Warranty Certificates

7. O&M Manual

---

## SECTION 10: APPENDICES

### Appendix A: Camera Schedule (Example)

| Camera ID | Location | Type | Resolution | IP Address |

| :--- | :--- | :--- | :--- | :--- |

| CAM-B1-01 | Basement 1 - Stair 2 | Bullet | 4K | 192.168.1.101 |

| CAM-B1-02 | Basement 1 - Stair 1 | Bullet | 4K | 192.168.1.102 |

| CAM-GF-01 | Ground Floor - Lobby | Dome | 4MP | 192.168.1.201 |

| CAM-1F-01 | 1st Floor - Lift Lobby 1 | Dome | 4MP | 192.168.1.301 |

| CAM-1F-02 | 1st Floor - Lift Lobby 2 | Dome | 4MP | 192.168.1.302 |

### Appendix B: Storage Calculation

```

Formula:

Storage (TB) = (Bitrate × 3600 × 24 × Days) / (8 × 1000 × 1000)

Example:

- Cameras: 64

- Bitrate: 4 Mbps (average)

- Days: 30

Storage = (64 × 4 × 3600 × 24 × 30) / (8 × 1000 × 1000)

= 663,552,000 / 8,000,000

= 82.9 TB

With RAID 5:

Total HDD = 82.9 / 0.75 = 110.5 TB

HDDs Required = 110.5 / 10 = 11 HDDs (10TB each)

```

### Appendix C: IP Address Schedule

| Device | IP Range | VLAN |

| :--- | :--- | :--- |

| Cameras | 192.168.1.100-200 | 10 |

| NVR | 192.168.1.10-20 | 10 |

| PoE Switches | 192.168.1.2-9 | 1 |

| VMS Server | 192.168.1.30-40 | 20 |

| Clients | 192.168.1.50-80 | 20 |

### Appendix D: Test Report Format

| Camera ID | Resolution | Night Vision | Motion | Recording | Result |

| :--- | :--- | :--- | :--- | :--- | :--- |

| CAM-B1-01 | 4K | PASS | PASS | PASS | ✅ |

| CAM-B1-02 | 4K | PASS | PASS | PASS | ✅ |

| CAM-GF-01 | 4MP | PASS | PASS | PASS | ✅ |

---

END OF DOCUMENT

Document Reference: SPOTS-120-CCTV-SPEC-001

Revision: R00

Date: September 2026

Prepared by: SPOTS ELECTROMECHANICAL WORKS LLC

---